## Slide 1
Course code : EEE-4123
High Voltage Engineering
Lecture-06
Topics
High Voltage Direct current (HVDC)
Presented by
Md. Shamim Sarker
Assistant Professor
Dept. of EEE, KUET

## Slide 2
Converter Arrangement and Operation
Figure: 6 Pulse bridge converter
n

## Slide 3
n

## Slide 4
Equation of voltage in each phase
Solving for DC Voltage, we get

## Slide 5
Converter Station
Figure: Schematic diagram of typical HVDC converter station
Conversion from AC to DC or from DC to AC take place

## Slide 6
Converter Station
Components of converter stations:
Converter Station:
 Two three phase converter bridge connected in series
 Total 12 valves are required
 Valves can be packeged as single, double or quadrivalve
 Valve firing signal is generated at the converter control at ground potential

## Slide 7
Figure: Twelve Pulse converter unit

## Slide 8
Converter Station
Components of converter stations:
2. Converter Transformer:
 Supply Power from AC network to DC network
 Valve side winding is converter bridge(One in star; Another is in delta)
 AC side windings of both are connected in star with their neutral ground

## Slide 9
Converter Station
Components of converter stations:
3. Filters:
 AC Filters: Passive circuit provides to bypass AC harmonics. Connected between phase and earth. Provide reactive power for converter.
 DC Filters : Connected between pole bus and neutral bus. Do not provide reactive power
High frequency filter: Bypass radio frequency component

## Slide 10
Converter Station
Components of converter stations:
4. Smoothing reactor: Large series reactor, used on DC side to smooth the dc current.
5. Reactive power source: Provide reactive power for the converter unit. We can use shunt capacitor for this.
6. Pole: path of DC which have the same polarity.
7. Ground Electrode: The ground electrodes are usually located at a distance of 15-55 km from the station

## Slide 11
Back to back HVDC station

## Slide 12
Two and Multi-terminal Converter station
2-TDC system
MTDC system
Advantages and Application of MTDC System

## Slide 13
Limitation of HVDC system
Transformers.
Cost of converter stations
Circuit breakers
Generation of harmonics
Cooling of HVDC substation
HVDC system control